## Sheet1
Location | Type | Text | High-Level | Annotations
0POP05-EO-ES12.SPROCEDURE STEPS.S13..S2..T1. | Centered Table | CHARGING PUMP STATUS ; RCS SUBCOOLING (°F)- BASED ON CORE EXIT TCs; ANY RCP RUNNING; NO RCP RUNNING;ONE HHSI PUMP RUNNING;TWO HHSI PUMPS RUNNING;THREE HHSI PUMPS RUNNING;ONE HHSI PUMP RUNNING;TWO HHSI PUMPS RUNNING;THREE HHSI PUMPS RUNNING; NONE RUNNING ; DO NOT STOP HHSI PUMP; 181 [191] ; 83 [97] ; DO NOT STOP HHSI PUMP; 193 [198] ; 96 [107] ; ONE RUNNING; 350 [354]; 138 [151]; 78 [92]; 349 [353]; 159 [167]; 90 [101]; TWO RUNNING; 298 [301]; 117 [130]; 74 [88]; 297 [300]; 135 [144]; 85 [97]; | CHECK IF One HHSI Pump Should Be Stopped: | Verify Table Conversion
0POP05-EO-EO30.SPROCEDURE STEPS.S7..S1..T1. | Centered Table | RUPTURED SG PRESSURE (PSIG); CORE EXIT TEMPERATURE (°F); 1285; 533 [518] ----------------------------; 1250; 529 [514]; 1200; 524 [509]; 1150; 517 [502]; 1100; 512 [497]; 1050; 505 [490]; 1000; 499 [484]; 950; 492 [477]; 900; 486 [471]; 850; 478 [463]; 800; 471 [456]; 750; 463 [448]; 700; 454 [439]; 650; 446 [431]; 600; 437 [422]; 550; 427 [412]; 500; 416 [401]; 450; 403 [388]; | INITIATE RCS Cooldown: | Verify Table Conversion
0POP05-EO-EC11.SPROCEDURE STEPS.S5..S2..T1. | Centered Table | RWST Level; Containment Pressure; NUMBER OF RCFCs RUNNING; NUMBER OF CONTAINMENT SPRAY PUMPS REQUIRED; GREATER THAN 75,000 gallons ;GREATER THAN 56.5 psig;All Available; 2; BETWEEN 6.5 psig and 56.5 psig ; 0 or 1; 2; 2 or 3; 1; 4, 5 or 6; 0;LESS THAN 6.5 psig; As Needed; 0; BETWEEN 33,000 and 75,000 gallons; GREATER THAN 6.5 psig ; 1, 2 or 3; 2; 4, 5 or 6; 0;LESS THAN 6.5 psig; As Needed; 0; LESS THAN 33,000 gallons ; N/A ; N/A ; 0 ; | MONITOR Containment Spray Requirements (Suction From RWST): | Verify Table Conversion
0POP05-EO-EC31.SPROCEDURE STEPS.S25..S2..T1. | Centered Table | CHARGING PUMP STATUS ; RCS SUBCOOLING (°F)- BASED ON CORE EXIT TCs; ANY RCP RUNNING; NO RCP RUNNING;ONE HHSI PUMP RUNNING;TWO HHSI PUMPS RUNNING;THREE HHSI PUMPS RUNNING;ONE HHSI PUMP RUNNING;TWO HHSI PUMPS RUNNING;THREE HHSI PUMPS RUNNING; NONE RUNNING ; DO NOT STOP HHSI PUMP; 181 [191] ; 83 [97] ; DO NOT STOP HHSI PUMP; 193 [198] ; 96 [107] ; ONE RUNNING; 350 [354]; 138 [151]; 78 [92]; 349 [353]; 159 [167]; 90 [101]; TWO RUNNING; 298 [301]; 117 [130]; 74 [88]; 297 [300]; 135 [144]; 85 [97]; | CHECK IF One HHSI Pump Should Be Stopped: | Verify Table Conversion
0POP05-EO-EC32.SPROCEDURE STEPS.S11..S2..T1. | Centered Table | CHARGING PUMP STATUS; RCS SUBCOOLING (°F); ONE HHSI PUMP RUNNING; TWO HHSI PUMPS RUNNING; THREE HHSI PUMPS RUNNING; NONE RUNNING ; DO NOT STOP HHSI PUMP ; 67 [79] ; 53 [65] ; ONE RUNNING ; 178 [192] ; 61 [73] ; 52 [64] ; TWO RUNNING ; 111 [125] ; 58 [70] ; 51 [63]; | CHECK IF One HHSI Pump Should Be Stopped: | Verify Table Conversion
0POP05-EO-FRH1.SPROCEDURE STEPS.S28..S2..T1. | Centered Table | CHARGING PUMP STATUS; RCS SUBCOOLING (°F); ONE HHSI PUMP RUNNING; TWO HHSI PUMPS RUNNING; THREE HHSI PUMPS RUNNING; NONE RUNNING ; DO NOT STOP HHSI PUMP ; 193 [198] ; 96 [107] ; ONE RUNNING ; 349 [353] ; 159 [167] ; 90 [101] ; TWO RUNNING ; 297 [300] ; 135 [144] ; 85 [97]; | CHECK If One HHSI Pump Should Be Stopped: | Verify Table Conversion
Location | Type | Text | High-Level | Annotations
EMG ES-01.SProcedure Steps.S1..T1. | AER Table | 1234567890; | Check Procedure EMG E-0, REACTOR TRIP OR SAFETY INJECTION - NOT IN EFFECT | Verify Table Conversion
EMG ES-01.SProcedure Steps.S2..R1..T1. | Centered Table | 1234567890; | Check AC Emergency Busses - AT LEAST ONE ENERGIZED | Verify Table Conversion
EMG ES-04.SProcedure Steps.S16..S2..T1. | Centered Table | CRDM FAN STATUS; REQUIRED RCS SUBCOOLING (°F); 2 OR 3 RUNNING FOR ENTIRE COOLDOWN; 75°F ; 0 OR 1 RUNNING DURING COOLDOWN; 125°F; | Continue RCS Cooldown And Depressurization: | Verify Table Conversion
EMG ES-04.SProcedure Steps.S25..S2..T1. | Centered Table | CRDM FAN STATUS; REQUIRED RCS SUBCOOLING (°F); 2 OR 3 RUNNING FOR ENTIRE COOLDOWN; 75°F ; 0 OR 1 RUNNING DURING COOLDOWN; 125°F; | Continue RCS Cooldown To Cold Shutdown: | Verify Table Conversion
EMG ES-04.SA.S2..T1. | Centered Table | INDICATED PZR LEVEL; PZR MULTIPLIER; RCS MULTIPLIER;91% TO 100%; 0.144; 0.856;81% TO 90%; 0.132; 0.868;71% TO 80%; 0.119; 0.881;61% TO 70%; 0.107; 0.893;51% TO 60%; 0.094; 0.906;41% TO 50%; 0.080; 0.920;31% TO 40%; 0.066; 0.934;21% TO 30%; 0.052; 0.948;11% TO 20%; 0.037; 0.963; 0% TO 10%; 0.022; 0.978; | Determine PZR and RCS multipliers from the following table: | Verify Table Conversion
EMG E-1.SProcedure Steps.S11..S2..T1. | Centered Table | CONTAINMENT PRESSURE ; FAN COOLERS RUNNING IN EMERGENCY MODE; SPRAY PUMPS REQUIRED;GREATER THAN 60 psig; ------; 2;BETWEEN 3 psig AND 60 psig AND INCREASING; ------ ; 2 ;BETWEEN 3 psig AND 60 psig AND DECREASING; LESS THAN 2; 2;; 2 OR MORE; 1;LESS THAN 3 psig; ------; 0; | Check If Containment Spray Should Be Stopped: | Verify Table Conversion
EMG ES-11.SProcedure Steps.S20..S2..T1. | Centered Table | SI PUMP STATUS; RCS SUBCOOLING (°F); ANY RCP RUNNING; NO RCP RUNNING; NONE RUNNING; 80 [125]; 95 [125]; ONE RUNNING; 50 [70]; 60 [75]; TWO RUNNING; 50 [70]; 55 [75]; | Check If One CCP Should Be Stopped: | Verify Table Conversion
EMG ES-11.SProcedure Steps.S21..S2..T1. | Centered Table | SI PUMP STATUS; RCS SUBCOOLING (°F); ONE CCP RUNNING; NO CCP RUNNING; ANY RCP RUNNING; NO RCP RUNNING; ANY RCP RUNNING; NO RCP RUNNING; ONE RUNNING; 125 [150]; 150 [175]; -----; -----; TWO RUNNING; 45 [60]; 50 [65]; 55 [75]; 60 [80]; | Check If SI Pumps Should Be Stopped: | Verify Table Conversion
EMG ES-11.SProcedure Steps.S22..S2..T1. | Centered Table | REQUIRED RCS SUBCOOLING (°F); ANY RCP RUNNING; NO RCP RUNNING; 112.5°F [ 137.5°F ]; 137.5°F [ 150°F ]; | Check If Normal Charging Should Be Established: | Verify Table Conversion
EMG ES-12.SProcedure Steps.S16..S3..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Verify Core Cooling: | Verify Table Conversion
EMG ES-13.SProcedure Steps.S9..S3..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Verify Core Cooling: | Verify Table Conversion
EMG E-3.SProcedure Steps.S12..T1. | Centered Table | LOWEST RUPTURED S/G PRESSURE (PSIG); TARGET CORE EXIT TEMPERATURE (°F); TARGET INTACT S/G PRESSURE (PSIG); TARGET CONDENSER STEAM DUMP CONTROLLER SETPOINT; GREATER THAN 1200; 519 [504]; 791 [691]; 5.27 [4.61]; 1100 TO 1199; 508 [493]; 717 [624]; 4.78 [4.16]; 1000 TO 1099; 496 [481]; 642 [557]; 4.28 [3.71]; 900 TO 999; 484 [469]; 573 [495]; 3.82 [3.30]; 800 TO 899; 470 [455]; 500 [430]; 3.33 [2.87]; 700 TO 799; 455 [440]; 430 [367]; 2.87 [2.45]; 600 TO 699; 438 [423]; 359 [304]; 2.39 [2.03]; 500 TO 599; 420 [405]; 294 [247]; 1.96 [1.65]; 400 TO 499; 398 [383]; 227 [188]; 1.51 [1.25]; 300 TO 399; 372 [357]; 163 [133]; 1.09 [0.89]; 275 TO 299; 364 [350]; 147 [118]; 0.98 [0.79]; | Determine Target Plant Conditions From Table Below: | Verify Table Conversion
EMG E-3.SProcedure Steps.S52..S1..T1. | Centered Table | PZR LEVEL; RUPTURED S/G(s) LEVEL; INCREASING; DECREASING; OFFSCALE HIGH; LESS THAN 23% [ 50% ] ;o Increase charging flow o Depressurize RCS using Step 53 ; Increase charging flow ;o Increase charging flow o Maintain RCS and ruptured S/G pressures equal; BETWEEN 23% [ 50% ] and 50%; Depressurize RCS using Step 53 ; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal; BETWEEN 50% AND 75% [ 61% ] ;o Depressurize RCS using Step 53 o Decrease charging flow; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal ; GREATER THAN 75% [ 61% ]; Decrease charging flow ; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal; | Control RCS Pressure And Charging Flow To Minimize RCS-To-Secondary Leakage: | Verify Table Conversion
EMG ES-32.SProcedure Steps.S9..S1..T1. | Centered Table | PZR LEVEL; RUPTURED S/G(s) LEVEL; INCREASING; DECREASING; OFFSCALE HIGH; LESS THAN 23% [ 50% ] ;o Increase charging flow o Depressurize RCS using Step 10 ; Increase charging flow ;o Increase charging flow o Maintain RCS and ruptured S/G pressures equal; BETWEEN 23% [ 50% ] and 50%; Depressurize RCS using Step 10 ; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal; BETWEEN 50% AND 75% [ 61% ] ;o Depressurize RCS using Step 10 o Decrease charging flow; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal ; GREATER THAN 75% [ 61% ]; Decrease charging flow ; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal; | Control RCS Pressure And Charging Flow To Minimize RCS-To-Secondary Leakage: | Verify Table Conversion
EMG ES-33.SProcedure Steps.S11..S1..T1. | Centered Table | PZR LEVEL; RUPTURED S/G(s) LEVEL; INCREASING; DECREASING; OFFSCALE HIGH; LESS THAN 23% [ 50% ] ;o Increase charging flow o Depressurize RCS using Step 12 ; Increase charging flow ;o Increase charging flow o Maintain RCS and ruptured S/G pressures equal; BETWEEN 23% [ 50% ] and 50%; Depressurize RCS using Step 12 ; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal; BETWEEN 50% AND 75% [ 61% ] ;o Depressurize RCS using Step 12 o Decrease charging flow; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal ; GREATER THAN 75% [ 61% ]; Decrease charging flow ; Turn on PZR heaters ; Maintain RCS and ruptured S/G pressures equal; | Control RCS Pressure And Charging Flow To Minimize RCS-To-Secondary Leakage: | Verify Table Conversion
EMG C-11.SProcedure Steps.S6..S2..T1. | Centered Table | RWST LEVEL ; CONTAINMENT PRESSURE ;FAN COOLERS RUNNING IN SLOW SPEED;SPRAY PUMPS THAT SHOULD BE RUNNING; GREATER THAN 36% ;GREATER THAN 60 PSIG; ---; 2; BETWEEN 27 PSIG AND 60 PSIG ; 0; 2; 2; 1; 4; 0; LESS THAN 27 PSIG; ---; 0; BETWEEN 6% AND 36% ;GREATER THAN 60 PSIG; ---; 2; BETWEEN 27 PSIG AND 60 PSIG ; 0; 1; 2; 1; 3; 0; LESS THAN 27 PSIG; ---; 0; LESS THAN 6%; ---; ---; 0; | Determine Containment Spray Requirements (Suction From RWST): | Verify Table Conversion
EMG C-11.SProcedure Steps.S23..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Check If ECCS Flow Can Be Terminated: | Verify Table Conversion
EMG C-11.SProcedure Steps.S37..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Verify Adequate RCS Makeup Flow: | Verify Table Conversion
EMG C-11.SProcedure Steps.S56..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Verify Adequate RCS Makeup Flow: | Verify Table Conversion
EMG C-11.SProcedure Steps.S59..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Depressurize All Intact S/Gs As Necessary To Inject Accumulators And Maintain RVLIS Indication: | Verify Table Conversion
EMG C-11.SC.S2..T1. | Centered Table | TIME AFTER RX TRIP; MINIMUM ECCS FLOW FOR DECAY HEAT REMOVAL; 1 HR; 380 GPM; 2 HR; 310 GPM; 4 HR; 250 GPM; 8 HR; 210 GPM; 16 HR; 180 GPM; 24 HR; 160 GPM; 36 HR; 140 GPM; 48 HR; 130 GPM; | Determine Required ECCS Flow From Table: | Verify Table Conversion | DW-95-023, AN 98-020 STPT CHANGE
EMG C-13.S3.0.S1. | Centered Table | References; |  | Verify Table Conversion
EMG C-13.SProcedure Steps.S14..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Verify Adequate RCS Makeup Flow: | Verify Table Conversion
EMG C-13.SProcedure Steps.S24..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Check If SI Can Be Terminated: | Verify Table Conversion
EMG C-13.SProcedure Steps.S37..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Verify Adequate RCS Makeup Flow: | Verify Table Conversion
EMG C-13.SProcedure Steps.S56..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Check If Cooldown Rate Is Adequate: | Verify Table Conversion
EMG C-13.SProcedure Steps.S58..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Depressurize All Intact S/Gs As Necessary To Inject Accumulators And Maintain RVLIS Indication: | Verify Table Conversion
EMG C-31.SProcedure Steps.S30..S2..T1. | Centered Table | SI PUMP STATUS; RCS SUBCOOLING (°F); ANY RCP RUNNING; NO RCP RUNNING; NONE RUNNING; 80 [125]; 95 [125]; ONE RUNNING; 50 [70]; 60 [75]; TWO RUNNING; 50 [70]; 55 [75]; | Check If One CCP Should Be Stopped: | Verify Table Conversion
EMG C-31.SProcedure Steps.S31..S2..T1. | Centered Table | SI PUMP STATUS; RCS SUBCOOLING (°F); ONE CCP RUNNING; NO CCP RUNNING; ANY RCP RUNNING; NO RCP RUNNING; ANY RCP RUNNING; NO RCP RUNNING; ONE RUNNING; 125 [150]; 150 [175]; -----; -----; TWO RUNNING; 45 [60]; 50 [65]; 55 [75]; 60 [80]; | Check If SI Pumps Should Be Stopped: | Verify Table Conversion
EMG C-31.SProcedure Steps.S32..S2..T1. | Centered Table | REQUIRED RCS SUBCOOLING (°F); ANY RCP RUNNING; NO RCP RUNNING; 112.5°F [ 137.5°F ]; 137.5°F [ 150°F ]; | Check If Normal Charging Should Be Established: | Verify Table Conversion
EMG C-32.SProcedure Steps.S14..S2..T1. | Centered Table | SI PUMP STATUS; RCS SUBCOOLING (°F); NONE RUNNING; 60 [80]; ONE RUNNING; 55 [70]; TWO RUNNING; 50 [65]; | Check If One CCP Should Be Stopped: | Verify Table Conversion
EMG C-32.SProcedure Steps.S15..S2..T1. | Centered Table | SI PUMP STATUS; RCS SUBCOOLING (°F); ONE CCP RUNNING; NO CCP RUNNING; ONE RUNNING; 75 [90]; -------; TWO RUNNING; 50 [65]; 50 [70]; | Check If SI Pumps Should Be Stopped: | Verify Table Conversion
EMG C-32.SProcedure Steps.S24..S4..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 82% NATURAL CIRCULATION RANGE; | Check If Charging Flow Should Be Controlled To Maintain Reactor Coolant Inventory: | Verify Table Conversion
EMG C-32.SProcedure Steps.S34..S3..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 82% NATURAL CIRCULATION RANGE; | Verify ECCS Flow Not Required: | Verify Table Conversion
EMG C-32.SFOLDOUT.S1..S1..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 82% NATURAL CIRCULATION RANGE; | SI REINITIATION CRITERIA | Verify Table Conversion | NC # is different from C-13 & that is correct
EMG C-33.SProcedure Steps.S13..S4..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Check If SI Can Be Terminated: | Verify Table Conversion
EMG C-33.SProcedure Steps.S23..S3..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Verify ECCS Flow Not Required: | Verify Table Conversion
EMG C-33.SProcedure Steps.S35..S3..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Check If SI Accumulators Should Be Isolated: | Verify Table Conversion
EMG C-33.SFOLDOUT.S1..S1..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | SI REINITIATION CRITERIA | Verify Table Conversion
EMG F-0.S3.0.S1. | Centered Table | References; |  | Verify Table Conversion
EMG FR-C2.SProcedure Steps.S7..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 68% FORCED FLOW RANGE; 3; 46% FORCED FLOW RANGE; 2; 32% FORCED FLOW RANGE; 1; 24% FORCED FLOW RANGE; | Check RVLIS Indication: | Verify Table Conversion
EMG FR-P1.SProcedure Steps.S11..S3..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Check If SI Can Be Terminated: | Verify Table Conversion
EMG FR-P1.SProcedure Steps.S26..S3..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Verify ECCS Flow Not Required: | Verify Table Conversion
EMG FR-P1.SProcedure Steps.S28..S4..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 84% FORCED FLOW RANGE; 3; 56% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 28% FORCED FLOW RANGE; 0; 69% NATURAL CIRCULATION RANGE; | Check If SI Accumulators Should Be Isolated: | Verify Table Conversion
EMG FR-I3.SProcedure Steps.S18..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 94% FORCED FLOW RANGE; 3; 60% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 26% FORCED FLOW RANGE; 0; 31% FORCED FLOW RANGE; 0; 95% NATURAL CIRCULATION RANGE; | Check RVLIS Indication: | Verify Table Conversion | CSF F-06 gives table with all RCPs listed
EMG FR-I3.SProcedure Steps.S28..S5..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 94% FORCED FLOW RANGE; 3; 60% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 26% FORCED FLOW RANGE; 0; 31% FORCED FLOW RANGE; 0; 95% NATURAL CIRCULATION RANGE; | Review Reactor Vessel Venting Termination Criteria: | Verify Table Conversion
EMG FR-I3.SProcedure Steps.S30..S2..T1. | Centered Table | RCPs RUNNING; REQUIRED RVLIS LEVEL; 4; 94% FORCED FLOW RANGE; 3; 60% FORCED FLOW RANGE; 2; 39% FORCED FLOW RANGE; 1; 26% FORCED FLOW RANGE; 0; 31% FORCED FLOW RANGE; 0; 95% NATURAL CIRCULATION RANGE; | Check RVLIS Indication: | Verify Table Conversion
EMG FR-I3.SA.S15..S1..T1. | Centered Table | RCS HOT LEG TEMPERATURE (°F); CF ; GREATER THAN 550; 1.34; 500 TO 549; 1.26; 450 TO 499; 1.20; 400 TO 449; 1.15; 350 TO 399; 1.11; 300 TO 349; 1.08; 250 TO 299; 1.05; 200 TO 249; 1.03; | Determine correction factor = CF: | Verify Table Conversion